Hermetic horizontal sliding door, type “EFA-HHS-CR®”

Manufacture, delivery and installation of a

Single leafed horizontal, hermetically sealing, sliding door, type ‘EFA-HHS-CR’, with electric drive and automatic control for heavy duty intensive usage in GMP controlled rooms up to a pressure difference of 30 Pa or as sealed closure inerting logistic systems.

Type “EFA-HHS-CR®”, EFAFLEX make

The “EFA-HHS-CR®” is clean room certified by the TÜV SÜD Cleancert GmbH for class 5 acc. to DIN ISO 14644-1 for particle sizes ≥ 0.1 μm.

The components of the door, which hermitically seal against each other, consist of frame construction and lintel-mounted guide rail with a slope cover, which is produced from corrosion- resistant, polished V2A stainless steel (1.4301 IIIC) as well as the roller-guided door leaf (bearings are maintenance-free).

The door leaf consists of an aluminium frame with styrofoam insulation and a 0.8mm thick, polished V2A stainless steel sheet metal.

The door leaf is equipped with a horizontal and vertical clip-on gasket seal. When opening the door is lifted slightly and moved to the left or right (option). When closing the door is lowered to the floor and against the construction by means of a guide roller in order to achieve hermetical sealing.

The frame is produced in an embracing design from 40mm to 300mm and as an L-profile for wall thicknesses over 300mm.

The door is driven by a 0.24 kW geared motor and controlled using a microprocessor control unit and frequency inverter.

OPENING SPEED:		approx. 0.8 m/s

CLOSING SPEED:		approx. 0.4 m/s

On-site connection to 230 V / 50-60 Hz. Fuse 16 A

Designed for 120,000 cycles (opening/closing operations) per annum.

Safety systems:

Intelligent closing edge safety via contact activation with door reversing mechanism and a safety light barrier at 200mm height. Additionally, two active infrared presence detectors on each side of the door opening as well as a safety photo cell at 200mm from floor.

A second photo cell at a height of 1000mm as well as another active infrared presence detector are available on option.

A manual emergency opening is possible at all times by using a handle

The provisions, standards and directives

According to DIN EN 13241-1, EN 14644, DIN EN 12453, DIN EN 1631,VDI 2083 and US Federal Standard 209.

for clear opening dimensions 	(min. 	W x H =    700 x 1,000 mm)

(max. 	W x H = 2,000 x 2,450 mm)

Width = ............... mm  x  Height = ............... mm

(installation width must always be 150 mm more than the required clear width of the opening)

Manufacturer:

EFAFLEX Tor- und Sicherheitssysteme GmbH & Co. KG

www.efaflex.com

Options for the hermetic horizontal sliding door, type “EFA-HHS-CR®”

Door leaf

- 900 x 900 mm tempered safety window, fitted flush into the door leaf

- rock wool insulation

- Finish made of 3.0mm thick high-pressure laminate available in different colours

(standard similar to RAL 1013)

- second safety photo cell at 1000mm

- Active infrared presence detector

Activators and signals

- Clean room compatible push buttons or contact-free switches in UP version,

- Radar sensors, active infrared presence detector (as safety on option)

- LED traffic light