HIGH SPEED SPIRAL DOOR, type „EFA-SST®-L EX“

Manufacture, delivery and installation of

High-speed spiral door, type „EFA-SST®-L EX“, with electro-mechanical high-performance door drive for heaviest, permanent industrial application at internal & external installation.

The door system mainly consists of:

Self-supporting lateral steel frames; steel parts generally galvanized, spiral-shaped door guidance

The load is transmitted on both sides: For achieving this, a synchronised shaft will be installed. For the exact, smooth and low-noise guidance of the hinge straps, ball-bearing precision rolling units have to be used. A sufficiently dimensioned tension spring mechanism, ensuring the weight balancing of the door leaf according to the standard DIN EN 12604 and a manual opening of the door (e.g. in the case of a power failure) is installed in the door frames.

This SPIRAL BODY (optional round or oval spiral-shape) is designed to guide the laths of the door leaf completely without contact and thus without wear and with best possible noise reduction.

The DOOR is driven by a geared motor which has to be developed as high-frequency motor. The positions of the door are permanently detected by means of non-wearing, inductive proximity switches (zone 1), or absolute encoder (zone 2) with the limits being determined electronically. Electro-mechanical limit switches are not permissible here.

Door leaf options:

Option 1 lath separation 151 mm (spiral body with round or oval spiral-shape):

Door leaf made of double-walled, aluminium laths, which are fixed onto hinge straps and moved vertically (i.e. up or down), surface anodized (E6/EV1).

Option 2 lath separation 225 mm (spiral body with round spiral-shape):

The door leaf consists of a frame made of anodised aluminium as wall as of a middle area which is made of transparent, single-walled acrylic glass. The visible surface of the door leaf must be at least 70 %, and optical clarity must be ensured permanently.

OPENING SPEED:	up to approx. 1.0 m/s

CLOSING SPEED:	up to approx. 0.5 m/s

The MICROPROCESSOR CONTROL is installed together with the integrated frequency converter in a separate steel cabinet, protection type IP 65. Connection to 230V and/or 400 V / 50 Hz power supply on-site. It’s MANDATORY that the control-unit is installed outside of the EX area !

Door-safety:

- Electric Safety contact edge, self-monitoring acc. to DIN EN 12453 in EX proof version

Its connection cable must be guided in a protective energy chain within the door frame.

-	Safety photocell in EX proof version, protectively integrated in the door frame

-	Emergency-STOP-button in ATEX version (On-wall industrial version)

EX-proof versions:

According to ATEX-guidelines RL 2014/34EU the door system is suitable to be used in:

- EX-area-Zone 1 (II 2G IIB T4 X)

- EX-area-Zone 2 (II 3G IIB T4 X)

(X: Temperature range-15°Cto+50°C)

Any electrical component (excluding control-unit) will have a ATEX-certificate.
The mechanical EX-parts will be supplied according to ATEX-zone.

Regulations pursuant to DIN EN 13241-1 are complied with;

Resistance to wind load pursuant to DIN EN 12424 up to class 4

Air permeability to DIN EN 12426, class 2

Airborne sound insulation according to DIN EN 7171 up to 23 dB(A)

(values depend on the door size and the equipment)

for clear opening dimensions

Width = ............... mm  x  Height = ............... mm

Manufacturer:

EFAFLEX Tor- und Sicherheitssysteme GmbH & Co. KG

www.efaflex.com