SCHNELLLAUF-SPIRALTOR, type „EFA-SST®-L EX“

Manufacture, delivery and installation of

High-speed spiral door, type „EFA-SST®-L EX“, with electro-mechanical high-performance drive unit for heavy-duty permanent industrial application, internal and external installation.

The door system mainly consists of:

Self-supporting lateral steel frames; steel parts generally galvanized, spiral-shaped door guidance

The load is transmitted on both sides: For achieving this, a synchronised shaft will be installed. For the exact, smooth and low-noise guidance of the hinge straps, ball-bearing precision rolling units have to be used. A sufficiently dimensioned tension spring mechanism, ensuring the weight balancing of the door leaf according to the standard DIN EN 12604 and a manual opening of the door (e.g. in the case of a power failure) is installed in the door frames.

This SPIRAL BODY (optionally round and oval spiral) is designed to guide the laths of the door leaf completely without contact and thus without wear and with best possible noise reduction.

The door is driven by a geared motor which has to be developed as high-frequency motor. The positions of the door are permanently detected by means of non-wearing, inductive proximity switches (Zone 1) respectively by absolute encoders (Zone 2), with the limits being determined electronically. Electro-mechanical limit switches are not permissible for this.

Door blade designs:

Variant1 Lath design 151 mm (Spiral body with round or oval spiral guidance):

Door blade made of double-walled aluminium laths, screwed onto hinge chains and moved vertically (i.e. up and down), surface of laths anodised (E6/EV1).

Variant2 Lath design 225 mm (Spiral body with round spiral guidance):

Door blade made of anodised aluminium frame (E6/EV1) as well as transparent single-walled infill made of acrylic glass. Door blade transparency up to 70%, permanent transparency has to be guaranteed.

OPENING SPEED:	up to approx. 1.0 m/sec.

CLOSING SPEED:	up to approx. 0.5 m/sec.

The MICROPROCESSOR CONTROL is installed together with the integrated frequency converter in a separate steel switch cabinet, protection type IP 65. Connection to 230V / 50 Hz power supply on-site. Installation of the control MUST be outside the explosion hazardous zone.

SAFETY SYSTEMS:

- Safety contact edge, self-monitoring according to DIN EN 12453, ATEX version.

Cabling has to be done in a protected way within an energy chain inside the door frame.

- Safety photo cell in ATEX version, safely protected in the door frames

- Emergency stop button in ATEX version (industrial version on finery)

Explosion protection:

The door system is suitable for installation according to ATEX guidelines RL 2014/34/EU in:

- Explosion hazardous atmospheres Zone 1 (II 2G IIB T4 X)

- Explosion hazardous atmospheres Zone 2 (II 3G IIB T4 X)

(X: installation and surrounding temperature -15°C up to +50°C)

All electric components (excluding control box) come with ATEX certification.
The mechanical ATEX equipment is designed according to classification of the zone.

Regulations pursuant to DIN EN 13241-1 are complied with;

Wind resistance pursuant to DIN EN 12424 up to class 4

Air permeability pursuant to DIN EN 12426 class 2

Airborne sound insulation according to DIN EN 7171 up to 23 dB(A)

(Values depend on door size and equipment)

for clear opening dimensions

Width = ............... mm  x  Height = ............... mm

Manufacturer:

EFAFLEX Tor- und Sicherheitssysteme GmbH & Co. KG

www.efaflex.com